Development of New Target Stations for the South African Isotope Facility
G. F. Steyna,1, L. S. Anthonya, F. Azaieza, S. Baarda, R. A. Barka, A. H. Barnarda, P. Beukesa, J. I. Broodryka
J. L. Conradiea, J. C. Cornella, J. G. De Villiersa, S. G. Dolleya, H. Du Plessisa, W. D. Duckitta, D. T. Fouriea, 
M. E. Hogana, I. H. Kohlera, J. J. Lawriea, C. Lussia, N. R. Mantengua, J. P. Miraa, K. V. Mjalia, H. W. Mosterta, C. Naidooa, F. Nemulodia, D. Saala, N. P. Stodarta, R. W. Thomaea, M. J. Van Niekerka, P. A. van Schalkwyka
aiThemba LABS, Old Faure Road, Somerset West, 7129, South Africa
Introduction
iThemba LABS is a multi-disciplinary research facility under the management of the National Research Foundation (NRF) of South Africa. The facility currently operates 6 accelerators at two campuses, located at Faure (near Cape Town) and Johannesburg. The main activities comprise research and training in the physical, biomedical and material sciences, provision of accelerator mass spectrometry (AMS) services, and the production of isotopes and radiopharmaceuticals for use in nuclear medicine. This presentation will discuss an initiative to achieve a three-fold increase in radioisotope production capacity.
The largest of the accelerators is a K=200 separated sector cyclotron (SSC) [1] that has been in operation for more than 30 years. This machine is operated in conjunction with two solid-pole injector cyclotrons, one for light ions and one for heavy ions and polarized protons. The SSC is a shared facility. It provides accelerated ion beams for radioisotope production, nuclear physics research and, until recently, for neutron and proton therapy. Nuclear physics experiments have mostly been conducted over weekends, the rest of the week scheduled for therapy (during the day) and production of both short-lived and long-lived radioisotopes (mostly at night).

A decision was recently taken that iThemba LABS would not continue with hadron therapy but would rather assist the medical community to pursue a dedicated proton therapy centre for South Africa. The significant progress in recent years on dedicated proton therapy centres as well as the reduction in cost of these facilities (single treatment-room facilities) will benefit the country much more if established at one of the large public hospitals. In contrast, while the therapy facilities at iThemba LABS are still fully functional, they are becoming aged and can only provide limited services due to the restricted beam time available for therapy. 
The sharing of beam time on the SSC is also limiting the other programmes. To increase the beam time for isotope production and nuclear physics research, the establishment of a new facility, currently known as the South African Isotope Facility (SAIF) has been proposed. The new facility will consist of two parts: 

1. The Accelerator Centre for Exotic Isotopes (ACE Isotopes) will be a dedicated facility for radioisotope production. A commercial high-current 70 MeV H- cyclotron for this purpose will free the SSC and allow an increase in beam time for nuclear physics and related research. 

2. The Accelerator Centre for Exotic Beams (ACE Beams) will be a radioactive ion beam (RIB) facility for nuclear physics research. The SSC will be used as a driver for an isotope separation on-line (ISOL) facility. A 66 MeV proton beam of up to 50 μA will be delivered by the SSC for producing radioactive beams from a target ion source. The first stage of this project will be a low-energy radioactive ion beam (LERIB) project without post acceleration. The second stage will be the post acceleration of the radioactive beams with a linear accelerator to energies of between 4 and 5 MeV per nucleon. Some of the funding has been secured for the development of LERIB and work on the project is in progress.
With the above “roadmap” for the future of iThemba LABS in place, a design study on new target stations for radionuclide production with a dedicated 70 MeV cyclotron commenced. This work is now in an advanced stage. 
The main aspects of the new stations for batch targets (encapsulated materials and solids) are discussed below. The experience gained on the existing bombardment infrastructure largely influenced the new target station design. A brief historical overview will therefore be given, followed by discussing the new station design and the changes necessary to the current facilities at iThemba LABS in order to accommodate them. 
Materials and Methods
Existing facilities
The routine isotope production programme with the SSC started in 1988 with the commissioning of the horizontal beam target station (HBTS, also called Elephant), producing short-lived radioisotopes such as 52Fe, 67Ga, 109Cd, 111In and 123I. Towards the late 1990s, production methods for the long-lived radioisotope 22Na were developed and commercialized. This was followed by the targetry development for 68Ge and 82Sr. In 1996 a second target station was designed and built for the bombardment of semi-permanent targets. This initially included 18F but that production was later transferred to a dedicated Siemens 11 MeV cyclotron. In 2006, the vertical beam target station (VBTS) was commissioned to exploit high-intensity proton beams delivered by the upgraded SSC. Target development for the VBTS focused on the relatively long-lived, high-value radioisotopes 22Na, 68Ge and 82Sr. Various tandem targets, e.g. Rb/Ga for 82Sr/68Ge production and Mg/Ga for 22Na/68Ge production, are routinely bombarded in the VBTS with 66 MeV proton beams with intensities up to 250 µA.
. 
When a beam splitter was commissioned in 2007, it allowed the simultaneous bombardment of four targets, i.e. beams on tandem targets in the HBTS and VBTS at the same time.
Thus, over the years, several upgrades were undertaken to increase the production yield, especially for the long-lived radioisotopes to meet an ever increasing market demand. The options for further growth on the SSC, however, have now been exhausted. Further growth can only be met by introducing a significant increase in allocated beam time, which would come at a large expense to the other programmes, or by procuring a dedicated cyclotron for isotope production. This last option was chosen and will be achieved with the ACE Isotopes facility.
ACE Isotopes

The new isotope production facility will make use of three concrete vaults previously occupied by the radiotherapy program, as shown in Fig. 1.
[image: image1.jpg]


[image: image7.png]



The layout of the ACE Isotopes facility is shown in Fig. 2: The cyclotron will be located in the centre vault, with the bombardment of targets taking place in the two adjacent vaults. This will ensure flexibility since the production vaults are independent of each other, thus production can continue in one vault while maintenance is being performed in the other.
Each production vault will contain two target stations. The stations can be classified as either
high intensity (up to 350 μA) for production of long-lived isotopes or medium intensity (up to 100 μA) for production of short-lived isotopes. To maintain uninterrupted bombardment of batch targets, two high-intensity stations (one per production vault) and one medium-intensity station will be required. The fourth station will be dedicated to experimental development work and semi-permanent targets. The four beamlines all have the same design. Extracted beam will pass through a switching magnet and then continues through a straight section of beam pipe to a target station. Two sets of quadrupole doublets per beamline will be used for focussing. A “wobbler” system for sweeping the beam over the target surface will be located after the last quadrupole. Diagnostic systems will include profile grids for low-intensity beams and non-destructive capacitive beam position monitors for high-intensity beams.
Figure 2: Layout of ACE Isotopes, showing the cyclotron vault (middle), production vaults (left and right) and the proposed target transport system.
New target stations
The transfer of the radioisotope production programme from the SSC to ACE Isotopes will take several years to complete. The existing target stations will continue to receive beam from the SSC while the new target stations are being built and commissioned.

Currently, the transfer of batch targets between the two existing target stations (HBTS and VBTS) and the processing hot-cell complex is by means of a Telelift rail system [2,3]. This system will be expanded to the two new production vaults. The existing transporter control system will also be modernized. 
The design of the new batch-target stations, shown in Fig. 3, is now in an advanced stage. The three planned stations will be identical in all respects except for the entrance collimator aperture, which will be smaller in the medium-intensity station. The local radiation shield will consist of complementary shielding materials, namely an inner iron shield, followed by borated paraffin wax as a middle layer, followed by an outer lead γ-ray shield. Monte Carlo radiation transport simulations provided the optimal layer thicknesses in order to achieve a dose attenuation factor of 3 orders of magnitude. 
The new target stations will all be fitted with a rotatable magazine that can hold three target holders. This will be a significant simplification in

[image: image8.jpg]



Figure 3: Cutaway view of the production station, with the beamline (left) and cooling-water pusher arm (right). The shielding consists of (a) an inner iron layer, (b) borated paraffin wax and (c) an outer lead shield.
comparison with the current HBTS magazine, the latter of which can hold nine target holders. Figure 4 shows a cross-sectional view of a target station as seen in the opposite direction to the beam direction. The magazine is shown with one target in the bombardment position (the lowest position) with all three target positions filled. The structure mounted on the right is a pneumatically controlled robot arm for transferring target holders between a Telelift transporter and the station. A close-up view of the target magazine is shown in Fig. 5. It can be rotated to put any of the target holders in the bombardment position or in the “transfer” position when operating the robot arm. 
[image: image2.emf]
Figure 4: Simplified cross-sectional view of a target station. The robot arm is on the right.
[image: image3.emf]
Figure 5: Close-up view of the target magazine.
A new 70 MeV tandem Rb/Ga prototype target (see Fig. 6) has recently been assembled and pressure-tested. It will be operated with a 20% higher cooling-water flow rate compared to the existing VBTS targets. The new prototype target capsules have an outer diameter of 40 mm, similar to the present VBTS targets, however provision is made to increase the diameter of future capsules up to 52 mm. This will enable an increase in beam current from present nominal values of 250 µA to more than 300 µA.
Figures 6 shows the encapsulated Rb and Ga targets mounted on a bayonet-mount plug, which in turn can be fitted onto a tandem target holder. The Rb metal is contained in a stainless steel capsule (grade 316) while the Ga target capsule is made from niobium [2]. Figure 7 shows an open target holder while Fig. 8 shows the closed target holder after the targets have been loaded. The 8 holes at the bottom of the holder are cooling-water inlet and outlet ports.
[image: image4.jpg]



Figure 6: The tandem Rb/Ga targets mounted on a bayonet-mount plug. 
[image: image5.jpg]



Figure 7: An open tandem target holder with the bayonet-mount plug removed.

[image: image6.jpg]



Figure 8: A closed tandem target holder with the bayonet-mount plug in position.
Results and Conclusion 
Some development work towards Phase 1 of the ACE Beams project has commenced. Most of the approvals for the ACE Isotopes project are in place but funding models are still being investigated. It is expected that funding issues will be resolved soon. A dedicated 70 MeV cyclotron for radioisotope production will free the SSC to focus exclusively on scientific research, including a new RIB programme. The completed SAIF facility will be positioned to realize a three-fold increase in isotope production capacity.
References
1.
A.H. Botha et al., Commissioning of the NAC separated-sector cyclotron, in Proc. 11th Int. Conf. on Cyclotrons and their Applications, Tokyo, Japan, Oct 1986, pp. 9-16.
2.
G.F. Steyn et al., A vertical-beam target station, Nucl. Instrum. Meth. A 727 (2013) 131-144.
3.
Telelift ETV System. URL: https://en.telelift-logistic.com/faq-engl.html.
Figure 1: Layout of the cyclotron facility at iThemba LABS, with ACE Isotopes (shaded blue), LERIB (green) and Phase 2 of ACE Beams (pink).








1Corresponding author, deon@tlabs.ac.za

